## Empty Tables for Assignment
table 3: Utilities
Utilities | Unit | Compressor |  | Pumps |  | Effective heat |  | Heat Ioss |  | Total
|  | MWh | GJ(p) | MWh | GJ(p) | 1000 m3 | GJ(p) | 1000 m3 | GJ(p) | GJ(p)
Electricity | MWh
Natural gas | 1000 m3
Total primary energy | GJ(p)
table 4: Accomodation Building A
Building A | Unit | Heating |  | Lighting |  | Ventilation |  | Total
|  | 1000 m3 | GJ(p) | MWh | GJ(p) | MWh | GJ(p) | GJ(p)
Electricity | MWh
Natural gas | 1000 m3
Total primary energy | GJ(p)
table 5: Accomodation Building B
Building B | Unit | Heating |  | Lighting |  | Office equipment |  | Total
|  | 1000 m3 | GJ(p) | MWh | GJ(p) | MWh | GJ(p) | GJ(p)
Electricity | MWh
Natural gas | 1000 m3
Total primary energy | GJ(p)
table 6: Accomodation Building C
Building C | Unit | Heating |  | Lighting |  | Total
|  | 1000 m3 | GJ(p) | MWh | GJ(p) | GJ(p)
Electricity | MWh
Natural gas | 1000 m3
Total primary energy | GJ(p)
table 7: Production Ceramics
Ceramics | Unit | Powder & Moulds |  | Firing |  | Sintering |  | Total
|  |  | GJ(p) |  | GJ(p) |  | GJ(p) | GJ(p)
Electricity | MWh
Natural gas | 1000 m3
Compressed air | MWh
Total primary energy | GJ(p)
table 8: Production Assembly
Assembly | Unit | Assembly
GJ(p)
Electricity | MWh
Natural gas | 1000 m3
Compressed air | MWh
Total primary energy | GJ(p)
table 9: Summary
Department | Allocated to end users
| Electricity | Natural gas | Compr. air
| (MWh) | (1000 m3) | (MWh)
Powder & Moulds
Firing
Sintering
Assembly
Utilities | Losses under Accom. & Prod.
Building A
Building B
Building C
Total
table 10: Check
| Allocated | Purchased | Difference
Electricity (MWh)
Natural gas (*1000 m3)
1 kWh = | 9 | MJ(p)
1 m3 = | 31.65 | MJ(p)

## Electricity
table 1: Electricity consumption measurements
Main | 7730 | Purchase
E1 | 6260 | Building A + Lighting & ventilation
E2 | 1320 | Lighting and ventilation
E3 | 910 | Utilities
E4 | 4100 | Sintering
E5 | 450 | Assembly, Soldering, Final assembly
E6 | 120 | Assembly

## Gas
table 2: Gas consumption measurement data (* 1000 m3)
Main | 1410 | Purchase
A1 | 620 | Firing

## Buildings
A |  | B
Ceramics |  | Offices
12000 | m2 | 2000 | m2
Assembly |  | C
8000 | m2 | Storage room
|  | 10000 | m2
D
Utilities

## Utilities
table 3: Utilities
Utilities | Unit | Compressor |  | Pumps |  | Effective heat |  | Heat Ioss |  | Total
|  | MWh | GJ(p) | MWh | GJ(p) | 1000 m3 | GJ(p) | 1000 m3 | GJ(p) | GJ(p)
Electricity | MWh | 878 | 7902 | 32 | 288
Natural gas | 1000 m3 |  |  |  |  | 513.5 | 16252.275 | 276.5 | 8751.225
Total primary energy | GJ(p) |  | 7902 |  | 288 |  | 16252.275 |  | 8751.225 | 33193.5
1 kWh = | 9 | MJ(p)
1 m3 = | 31.65 | MJ(p)
Electricity for central heating pumps and compressors
Meter E3 gives the electricity consumption for building D. This is consumed by pumps and compressors. There is no submetering which means we must use estimates as follows:
Pumps | 8 kW power rating at 4,000 hours: consumption 32 Mwh (per year)
Compressors | The consumption of the compressor is (with the aid of the electrical meter chart) determined as follows: (meter E3) - 32 = 910 - 32 = 878 MWh
This amount is allocated to production as follows:
(Estimation on the basis of machine data)
30% for assembly: 263 MWh,
70 % for Powder and Mould production: 615 MWh.
Natural gas consumption (see meter chart, figure 4):
Main meter - A1 (consumption production) = 1410 - 620 = 790,000 m3
Boiler efficiency is approximately 65 %, therefore 35 % is heat loss (276,000 m3) and 65 % is effective heat (514,000 m3).

## Accomodation A
table 4: Accomodation Building A
Building A | Unit | Heating |  | Lighting |  | Ventilation |  | Total Utilities
|  | 1000 m3 | GJ(p) | MWh | GJ(p) | MWh | GJ(p) | GJ(p)
Electricity | MWh |  |  | 690 | 6210 | 630 | 5670
Natural gas | 1000 m3 | 493.75 | 15627.1875
Total primary energy | GJ(p) |  | 15627.1875 |  | 6210 |  | 5670 | 27507.1875
1 kWh = | 9 | MJ(p) | (= 3,6 MJ/kWh / 40%, which means assuming an efficiency of 40% for the production of electricity)
1 m3 = | 31.65 | MJ(p)
Heating
Estimate of heat distribution between the buildings on the basis of m2 ratios (inclusing loss):
Building | m2 surface
A | 20000
B | 2000
C | 10000
Total | 32000
Exclude production energy!
Electricity total: Meter E2 1320 MWh (Lighting and Ventilation)
Estimated ventilation: 6 x at 21 Kw and 5,000 hours = 630 MWh
The rest is lighting: 1320 - 630 - 690 MWh

## Accomodation B
table 5: Accomodation Building B
Building B | Unit | Heating |  | Lighting |  | Office equipment |  | Total Utilities
|  | 1000 m3 | GJ(p) | MWh | GJ(p) | MWh | GJ(p) | GJ(p)
Electricity | MWh |  |  | 60 | 540 | 120 | 1080
Natural gas | 1000 m3 | 49.375 | 1562.7188
Total primary energy | GJ(p) |  | 1562.7188 |  | 540 |  | 1080 | 3182.7188
1 kWh = | 9 | MJ(p)
1 m3 = | 31.65 | MJ(p)
Heating
Estimate of heat distribution between the buildings on the basis of m2 ratios (inclusing loss):
Building | m2 surface
A | 20000
B | 2000
C | 10000
Total | 32000

## Accomodation C
table 6: Accomodation Building C
Building C | Unit | Heating |  | Lighting |  | Total Utilities
|  | 1000 m3 | GJ(p) | MWh | GJ(p) | GJ(p)
Electricity | MWh |  |  | 380 | 3420
Natural gas | 1000 m3 | 246.875 | 7813.5938
Total primary energy | GJ(p) |  | 7813.5938 |  | 3420 | 11233.5938
1 kWh = | 9 | MJ(p)
1 m3 = | 31.65 | MJ(p)
Heating
Estimate of heat distribution between the buildings on the basis of m2 ratios (inclusing loss):
Building | m2 surface
A | 20000
B | 2000
C | 10000
Total | 32000
Lighting
B + C together = Purchase - E1 - E3 = 7730 - 6260 - 910 = 560 MWh
Lighting far building C (building C has no ventilation): 560 - building B = 560 - (60 + 120) = 380 MWh

## Production Ceramics
table 7: Production Ceramics
Ceramics | Unit | Powder & Moulds |  | Firing |  | Sintering |  | Total Utilities
|  |  | GJ(p) |  | GJ(p) |  | GJ(p) | GJ(p)
Electricity | MWh | 340 | 3060 | 50 | 450 | 4100 | 36900 | 40410
Natural gas | 1000 m3 |  |  | 620 | 19623 |  |  | 19623
Compressed air | MWh | 614.6 | 5531.4 |  |  |  |  | 5531.4
Total primary energy | GJ(p) |  | 8591.4 |  | 20073 |  | 36900 | 65564.4
1 kWh = | 9 | MJ(p)
1 m3 = | 31.65 | MJ(p)
Electricity
Powder & Moulding + Firing together = E1 - E4 - E5 - E2 = 6260 - 4100 - 450 - 1320 = 390 MWh
Firing = 2 x 5 kW fans at 5000 hours = 50 MWh
Sintering = E4 = 4100 MWh
Compressed air
The following division is estimated on the basis of machine data: 30% for Assembly and 70 % for Powder and Moulds production.
This gives: Assembly 263 MWh, Powder and Moulds 615 MWh (see caIculation at Utilities).
Natural gas
Gas meter A1 for Firing.

## Production Assembly
table 8: Production Assembly
Assembly | Unit | Assembly
GJ(p)
Electricity | MWh | 450 | 4050
Natural gas | 1000 m3
Compressed air | MWh | 263.4 | 2370.6
Total primary energy | GJ(p) |  | 6420.6
1 kWh = | 9 | MJ(p)
1 m3 = | 31.65 | MJ(p)
Assembly
It can be seen from meter E5 (= 5% of the energy consumption) that the assembly hall is a minor consumer.
For this reason, the division of assembly into process steps is not necessary. The data for meter E6 are therefore deliberately not used.

## Checks
Department | Allocated to end users
| Electricity | Natural gas | Compressed air
| (MWh) | (1000 m3) | (MWh)
Powder & Moulds | 340 | 0 | 614.6
Firing | 50 | 620 | 0
Sintering | 4100 | 0 | 0
Assembly | 450 | 0 | 263.4
Utilities | 32 | (allocated to Accommodation) | (allocated to Production)
(only includes pumps which have not been allocated yet)
Building A | 1320 | 493.75 | 0
Building B | 180 | 49.375 | 0
Building C | 380 | 246.875 | 0
Total | 6852 | 1410 | 878
| Allocated | Purchased | Difference
Electricity (MWh) | 7730 | 7730 | 0%
Natural gas (*1000 m3) | 1410 | 1410 | 0%